## Cover Page
SPECIFICATIONS AND BILL OF QUANTITIES WITH ENGINEERING ESTIMATE
PROJECT:
GAMBELA PRIMARY HOSPITAL PEDIATRIC WARD
LOCATION:
GAMBELA, ETHIOPIA
OWNER:
DOCTORS WITH AFRICA- CUAMM
Prepared by:- Solomon Tesfay
2024-08-20

## preamble to BOQ
Preamble to the Bill of Quantities
1. The Bill of Quantities shall be read in conjunction with the Drawings and Technical Specifications.
2. The Bill of Quantities contains the following part Bills and Schedules:
a. Bill No. 1 – Gambela Primary Hospital Pediatric Ward
3. The Quantities given in the Bill of Quantities are estimated and provisional, and are given to provide a common basis for bidding. The estimated contract quantity of each item of works will be set at the time of contract signing. In addition to this the basis of payment will be the actual quantities of work ordered and carried out, as measured by the Contractor and verified by the Engineer and valued at the rates and prices bid in the priced Bill of Quantities, where applicable, and otherwise at such rates and prices as the Engineer may fix within the terms of the Contract.
4. The rates and prices bid in the priced Bill of Quantities shall, except insofar as it is otherwise provided under the Contract, include all Constructional Plant, Labor, supervision, materials, erection, maintenance, insurance, profit, taxes, and duties, together with all general risks, liabilities, and obligations set out or implied in the Contract.
5. A rate or price shall be entered against each item in the priced Bill of Quantities, whether quantities are stated or not. The cost of Items against which the Contractor has failed to enter a rate or price shall be deemed to be covered by other rates and prices entered in the Bill of Quantities.
6. The rates in this Bill of quantities shall consider all incidental works required to protect existing structures.
7. Items associated with a priced item necessary for its satisfactory fixing shall be considered as included in the rate of the item.
8. The rates given for Provisional Quantities (PQ) will be binding if the client decides to incorporate these works as additional works.
9. The whole cost of complying with the provisions of the Contract shall be included in the Items provided in the priced Bill of Quantities, and where no Items are provided, the cost shall be deemed to be distributed among the rates and prices entered for the related Items of Work.
10. The Overhead & risk and the gross profit for variation orders will be 35% .
11. General directions and descriptions of work and materials are not necessarily repeated nor summarized in the Bill of Quantities. References to the relevant sections of the contract documentation shall be made before entering prices against each item in the priced Bill of Quantities.
12. The method of measurement of completed work for payment shall be in accordance with Standard Methods of Measurement ECPN-4.
13. The Bill of Quantities contains items
a. Supplied and installed by the Prime contractor
b. Provisional Quantities Supplied and installed by the Prime contractor
14. Provisional Sums included and so designated in the Bill of Quantities shall be expended in whole or in part at the direction and discretion of the Engineer.
15. The duties and responsibilities of the Prime Contractor for items 13(b) above are deemed to be covered by the Contractor’s charge indicated in here. The duties and responsibilities of the Prime Contractor in addition to those indicated in the Bill of Quantities are:-
a. Handle and store materials at site both for prime contractor, the Client and nominated sub-contractor works.
b. Provide utilities like power, water and other necessary utilities for use by the Client and nominated sub-contractors.
c. Provide within the site transport and lifting equipment for all loading and unloading purposes and all required transportation within the site as required by the Client and nominated sub-contractors.
d. Provide scaffolding, ladder, etc as needed
e. Execute any incidental works, like concrete work, earthwork, finishing, patching, and chiseling as required by the Client and nominated sub- contractors.
f. Removal of debris and clean the site at completion
16. Errors will be corrected by the Employer for any arithmetic errors in computation or summation as follows:
(a) where there is discrepancy between amounts in figures and in words, the amount in words will govern
(b) where there is a discrepancy between the unit rate and the total amount derived from the multiplication of the unit price and the quantity, the unit rate as quoted will govern.
17. Rock is defined as all materials which, in the opinion of the Engineer, require blasting, or the use of metal wedges and sledgehammers, or the use of compressed air drilling for their removal, and which cannot be extracted by ripping with a tractor of at least 150 brake hp with a single, rear-mounted, heavy-duty ripper.
18. A type of bonding agent used for bonding old concrete to newly fresh one should get approval before application and the cost in connection with the bonding old concrete to newly fresh one shall be born by the Contractor.
19. All provision for sanitary pipe passage, Electrical and Sanitary ducts and provision of sleeves will have to be done during concrete works as per the Electrical and Sanitary drawings and they are deemed to be included in the other rates and prices entered in the Bill of Quantities.
20. The Contractor is responsible for the detail assessment of the Site conditions and any measure to be taken is included in the rates.
21. The removal of Surplus excavated material shall be to an appropriate place away from the construction site. The contractor shall also make arrangement to damp this surplus excavated material to the owner place by the Direction of the Resident Engineer.
22. The Contractor shall submit catalogues with full description for Items under all Divisions which include, but are not limited to: Finishing Materials, Electrical, Sanitary fittings & Equipments and shall get approval by the Engineer before purchasing or ordering.
23. All Electrical and Sanitary works /installation/ shall be done by experienced staff or specialized sub-contractor or personnel who have a minimum of eight years experience with similar works & this has to be approved by the Engineer based on their CVs & educational background and certification and recommendation and/or supervision by suppliers.
24. All Electrical and Sanitary works shall be tested & commissioned prior to filling chiseled cavities, installing ceilings, covering vertical & horizontal ducts & back filling trenches. The Contractor shall be fully responsible for all systems.
25. The Prime contractor shall submit samples of all finishing materials installed by himself and by nominated sub-contractors for approval by the Engineer and the Employer.

## Summary
SUMMARY OF PRICES
01. EXCAVATION AND EARTH WORK | Birr | 0
02. CONCRETE WORK | Birr | 0
03. MASONRY WORKS | Birr | 0
04. ROOFING | Birr | 0
05. CARPENTERY AND JOINERY | Birr | 0
06. METAL WORKS | Birr | 0
07. STEEL WORK | Birr | 0
08. WALL AND FLOOR FINISHING | Birr | 0
09. PAINTING | Birr | 0
10. SANITARY WORKS | Birr | 0
11. ELECTRICAL WORK | Birr | 0
SERVICE SUM | Birr | 0
15% VAT | Birr | 0
GRAND TOTAL | Birr | 0
Consultant's estimation for the realization of the civil works is 6 months
2660
|  |  | 60 | 28500
60

## BOQ
BILL OF QUANTITY - Gambela Primary Hospital Pediatric Ward
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | QUANTITY
01 | EXCAVATION AND EARTH WORK
EXCAVATION WORKS
* The contractor is responsible for covering any costs incurred due to damage of utility lines and care shall be taken for all existing utilities that could be covered or exposed to view throughout the project execution period.
1.1 | EXCAVATION AND GET OUR
1.1.1 | REMOVAL OF TOP SOIL
| Removal of Top Soil: The top soil shall be removed to the specified depth (200-300mm as directed by the Engineer) leaving area clear off any vegetable soil. The removal of top soil shall be measured by the area occupied by the work to be placed on the cleared area. Removal of top soil shall be understood as including the disposal of surplus material or stock piling and wheel spreading of top soil at later stages as directed by the Engineer. | m² | 191.295 |  | 0
1.1.2 | EXCAVATION IN ORDINARY SOIL
* Excavation shall mean the excavation and get out of the soil. Excavation in ordinary soil shall be measured by volume as the net void created by the excavation with deduction made for existing voids. * "Ordinary Soil" shall mean material yielding to ordinary excavation machinery or pick axes. * "Boulder" shall mean isolated volume of hard rock in ordinary soil and soft rock or above ground less than 1/2 cubic meter in volume.
1.1.2.1 | Bulk Excavation in Ordinary Soil: Bulk excavation to reduce the Natural ground Level to a depth not exceeding 100cm from reduced level. | m³ | 153.05 |  | 0
1.1.2.2 | Pit Excavation in ordinary soil: Pit excavation for isolated footing to a depth not exceeding 2000mm from reduced level. | m³ | 31.5 |  | 0
1.1.2.3 | Trench Excavation in Ordinary Soil: Trench excavation for the peripheral masonry wall to retain fill under ground slab. The depth of trench is not exceeding 1500cm from reduced level. | m³ | 18.03 |  | 0
1.2 | BACK FILL
* Fill to excavations or to make up level shall be made in suitable material approved by the Engineer and capable of being compacted. Þ Fill shall be placed in successive stages of not exceeding 200mm and watered and compacted to approval by the Engineer. * The compaction achieved in filling shall be measured in accordance with the standard practice. The In situ moisture content and density shall be compared with laboratory test results of modified AASHO T147 performed on samples of the selected material. * The minimum relative compaction to be achieved in the compacted area shall be 95% maximum dry density and the moisture content shall be within the range of 95% dry density. The moisture content of the fill material shall be adjusted as necessary to achieve the required compaction. Any material which after repeated compaction, does not fulfill the requirements, shall be removed and replaced. * The final levels of fill shall be adjusted, graded and prepared to receive bedding to be laid on fill. Fill shall be measured as equal to the net volume of void to be filled and shall be understood as including the stockpiling and haulage of material from location of fill.
1.2.1 | Selected borrowed fill - Suitable non-expansive well graded soil or granular material with no rock lumps imported from outside and approved by the Engineer. Fill works Is under floor slab and around footing pad as well a around foundation column. | m³ | 153.7304 |  | 0
1.3 | DISPOSAL
* All unsuitable and surplus suitable material arising from excavations shall be disposed off when instructed by the Engineer. * Disposal shall be made to tips directed by the Engineer or indicated in the document. In the absence of direction from the Engineer or indication in the documents, it is the contractor’s responsibility to identify the appropriate tip and dispose the material. * Disposal shall be understood to include stock piling, loading, transporting, dumping and wheel spreading at tip. Disposal shall be measured as the net volume arising from the void created by the excavation, less excavated material backfill, filled and wheel spread within site or left stockpiled.
1.3.1 | Cartaway surplus excavated material to a place where the administration has allotted for disposal. The contractor is responsible for permission from relevant authorities. | m³ | 240.84 |  | 0
1.4 | SUNDRY ITEMS
1.4.1 | HARDCORE AND STONE FILLERS
* Hard core shall be sound approved stone of specified finishing thickness and placed as directed by the Engineer and finished blinded with 20mm crushed aggregate. * Hard core shall be measured by the area of the surface on which it is laid if the finished thickness does not exceed 300mm. Hard core and stone filling exceeding 300mm thickness shall be measured by the volume of void filled by the hard core or stone chipping. * The girths of sinking shall be taken as the surface area of hard core where such sinking occur.
1.4.1.1 | Hardcore under Ground floor slab to a thickness of 25cm and blinded with 20mm crushed aggregate. | m2 | 110.03 |  | 0
01 | SUB TOTAL EXCAVATION & EARTH WORK ETH BIRR |  |  |  | 0
02 | CONCRETE WORKS
2.1 | Cast in Place Concrete
Cast in place concrete is concrete premixed at a batching plant and transported to the work site or concrete whose ingredients are transported to the site and mixed just before casting in place. Provide cement, aggregate, water admixture, labor equipment and tools for cast in place concrete as required for the satisfactory installation of the works. Quality Assurance 031 Standards Comply with the following standards. ES C. D5 201General Requirement, Portland cement, ES C. D8 490Methods of Sampling and testing Portland cement, ESI ES C. D3 201Normal Concrete aggregate, ESI ASTM C260 Air-entraining admixtures, ASTM C494 Water-reducing, retarding and accelerating admixtures. ASTM C94Mixing water for concrete. ASTM C330 Light weight aggregate for structural concrete
2.1.1 | 50mm thick C-5 lean concrete with minimum cement content of 150kg/m3 of concrete under
2.1.1.1 | Under Isolated footing | m2 | 16.94 |  | 0
2.1.1.2 | Under Stone Masonry | m2 | 25.75 |  | 0
2.1.1.3 | Under Grade beam | m2 | 9.6625 |  | 0
2.1.2 | REINFORCED CONCRETE
2.1.2.1 | REINFORCED CONCRETE GRADE C-25 (25 MPa) cast into formworks and vibrated around rod reinforcement bars. NB: Form work and reinforcement steel will measured elsewhere.
2.1.2.1.1 | In Isolated footing | m³ | 6.3 |  | 0 | 735.6
2.1.2.1.2 | In foundation Column | m³ | 1.302 |  | 0
2.1.2.1.3 | In Ground Column | m³ | 2.76 |  | 0
2.1.2.1.4 | In ground floor slab | m² | 110.03 |  | 0
2.1.2.1.5 | In grade beam | m³ | 5.47 |  | 0
2.1.2.1.6 | In Top tie Beams | m³ | 5.47 |  | 0
2.1.2.2 | FORMWORK FOR CONCRETE
Formwork shall mean temporary support construction for in-situ concrete, designed and constructed in timber or metal whichever is appropriate and capable of withstanding the live and dead loads imposed on it and fully preventing leakage of concrete. The work includes: Construction and removal of formwork Making good of concrete honeycombs. Making good of concrete surfaces to attain the standard of finish desired by the specified type of formwork.
2.1.2.2.1 | For Isolated Footing Pad | m2 | 25.2 |  | 0
2.1.2.2.2 | For Foundation column | m2 | 17.5 |  | 0
2.1.2.2.3 | Formwork to Grade Beam | m2 | 51.69 |  | 0
2.1.2.2.4 | For Ground column | m2 | 46.8 |  | 0
2.1.2.2.5 | For Top Tie Beam | m2 | 51.69 |  | 0
2.1.2.3 | REINFORCEMENT BARS
Reinforcement work shall be understood as the supply and fixing of reinforcement bars, including ties and chairs. The steel bars shall be high tensile (Grade S-420) hot rolled deformed Reinforcement Steel bar
2.1.2.3.1 | Rebar Diameter 6mm | kg | 0 |  | 0
2.1.2.3.2 | Rebar Diameter 8mm | kg | 1132.8205 |  | 0
2.1.2.3.3 | Rebar Diameter 10mm | kg | 0 |  | 0
2.1.2.3.4 | Rebar Diameter 12mm | kg | 261.072 |  | 0
2.1.2.3.5 | Rebar Diameter 14mm | kg | 1495.7456 |  | 0
2.1.2.3.6 | Rebar Diameter 16mm | kg | 0 |  | 0
2.1.2.3.7 | Rebar Diameter 20mm | kg | 0 |  | 0
2.1.2.3.8 | Rebar Diameter 24mm | kg | 0 |  | 0
2.2 | CONCRETE ANCILLARIES
2.2.1 | EXPANSION JOINTS
Expansion joints shall be formed between the concrete faces, or between concrete, by means of incorporating in the formwork an approved impregnated Chipwood/fiberboard or other filler to the thickness of 20mm. The Exposed edges of expansion joints shall be sealed. Filler boards shall be adequately wound into adjoining concrete to prevent their falling out when the joint opens. In-situ ground slabs laid on ground floor shall be cast in bays 6m x 6m (36m2 in area). The layout of construction joints in the slab shall be approved in advance
2.2.1.1 | Supply and fix 8mm thick and 100mm deep Chipwood/styrophom expansion joint filler b/n grade beam & ground floor slab. Price shall include all the necessary sealants and wear protection coats with all incidental works. | ml | 117.25 |  | 0
02 | SUB TOTAL CONCRETE WORK ETH BIRR |  |  |  | 0
03 | MASONRY
3.1 | STONE FOR MASONRY
Stone obtained from quarries approved by the Engineer shall be hard & sound, free from vents, cracks, fissures, discoloration, or other defects that will adversely affect strength or appearance. Stone chips out of which shaped stone are to be produced shall not be less than 450mm average and 380mm individual length.
3.1.1 | Stone masonry Concealed from View: 50cm thick stone masonry bedded in cement mortar (1:3) mix. price shall include cement mortar. | m³ | 38.63 |  | 0
3.2 | HOLLOW & SOLID CONCRETE BLOCKS
3.2.1 | Hollow block - (CLASS B, Average strength of 6 Blocks 35kg/cm2, Minimum strength of Individual Block 32kg/cm2
3.2.1.1 | 200mm thick class 'B' H.C.B wall bedded and jointed in cement mortar (1:3) both side left for appropriate finishing. | m² | 99.14 |  | 0
3.2.1.2 | 150mm thick class 'B' H.C.B wall bedded and jointed in cement mortar (1:3) both side left for appropriate finishing. | m² | 153.75 |  | 0
03 | SUB TOTAL MASONRY WORK ETH BIRR |  |  |  | 0
04 | ROOF WORK
4.1 | Supply and fix roof cover in precoated or galvanized EGA 400,0.4mm thick fixed to steel lattice purlin. Price shall include ridge cap, Dia 6mm fixing J-bolts and water proof washers.(purlin measured in horizontal projection) | m² | 156.315 |  | 0
4.2 | Supply and fix G-28 galvanized flat metal sheet gutter as per the detail drawing. price shall include all the necessary accessories, metal bracket, one coats of antirust .Development length =100cm | m² | 40 |  | 0
04 | SUB TOTAL ROOF WORK ETH BIRR |  |  |  | 0
05 | CARPENTRY & JOINERY
5.1 | Carpentry and Ceiling Works
5.1.1 | Supply, assemble and fix Gypsum Board Ceiling. Price shall include all necessary accessories to complete the work. Material sample, pattern design and Methodology should be approved by the engineer. | m² | 150.675 |  | 0
05 | SUB TOTAL CARPENTRY AND JOINERY WORK ETH BIRR |  |  |  | 0
06 | METAL WORK
6.1 | Aluminum doors, windows and curtain walls
Aluminum windows and doors made of extruded profiles of 6060 standard of UNI3569 HB65 norms dimensional tolerance and 1.6mm thickness of the aluminum frame. Aluminum profile shall be of Approved color with brushed finish cut and assembled to the sizes and shapes shown on the schedule of windows and doors. Manufacturing of the door and windows subject to approval of shop drawings to be provided by the Contractor. Price shall include 4mm thick nonreflective tinted glass, approved type of locks, necessary door stopper, and handle. All shall be according to the detail drawing. Hinges, Locks, Profiles and all important accessory samples should approved by the architect.
Standards Comply with the following standard. Hot dip galvanized coating on iron and steel articles BS 729 Anodic oxidation coating on Aluminum BS 1615 Anodic oxide coating on Aluminum for external architectural application BS 3987 Wrought steel for mechanical & allied engineering purposes BS 970
6.1.1 | Aluminum Doors
6.1.1.1 | Aluminum door type D1, size 155*280cm | No | 1 |  | 0
6.1.1.2 | Aluminum door type D2, size 150*280cm | No | 3 |  | 0
6.1.1.3 | Aluminum door type D3, size 75*280cm | No | 3 |  | 0
6.1.1.4 | Aluminum door type D4, size 75*280cm | No | 1 |  | 0
6.1.1.5 | Aluminum door type D5, size 65*280cm | No | 2 |  | 0
6.1.2 | Aluminum Window
6.1.2.1 | Aluminum Window Type W-1 size 100cm x 200cm | No | 6 |  | 0
6.1.2.2 | Aluminum Window Type W-2 size 300cm x 40cm | No | 2 |  | 0
6.1.2.3 | Aluminum Window Type W-3 size 40cm x 40cm | No | 2 |  | 0
6.1.2.6 | Aluminum Window Type W-4 size 120cm x 200cm | No | 2 |  | 0
06 | SUB TOTAL METAL WORK ETH BIRR |  |  |  | 0
07 | STEEL WORK
The following shall be provided as required for the satisfactory completion of the works. * Structural steel profiles, welding consumables, bolts, nuts and washer and Grouting concrete. * Labor for fabrication, assembly and erection. * Equipment, tools, scaffolding necessary for fabrication, assembly and erection.
STANDARDS Comply with the following standards, or equivalent: - * Welded cold-formed steel Structure hollow sections BS 6363 * Weldable structure steels BS 4360 * Structural use of steel in buildings BS 5950 * Electrodes for manual metal arc welding BS 639 * Black hexagonal bolts, screws and nuts BS 4190 * Metal arc welding of carbon and carbon manganese steels BS 4620
TESTS Tests to verify the grade and mechanical properties of the structural steel and welding of fabricated steel shall be carried out if required by the Engineer. Test samples shall be those randomly selected by the Engineer. The specific requirements of testing as detailed in BS 4360 shall be followed, to the extent determined by the Engineer.
7.2 | Truss Structure
7.2.1 | Truss, T1
7.2.1.1 | RHS 60*60*3mm for Horizontal truss member | kg | 394.6509 |  | 0
7.2.1.2 | RHS 50*50*2.5mm for Vertical and Diagonal truss member | kg | 201.3525 |  | 0
7.2.2 | Truss, T2
7.2.2.1 | RHS 40*40*2.5mm for Horizontal truss member | kg | 28.5544 |  | 0
7.2.2.1 | RHS 40*40*2.5mm for Vertical and Diagonal truss member | kg | 2.355 |  | 0
7.3 | Lattice Purlins:
7.3.1 | RHS 30mm x 30mm x 2mm top and bottom Horizontal members | kg | 495.1654 |  | 0
7.3.2 | RHS 25*25*2mm for Vertical and Diagonal Purlin members | kg | 99.548 |  | 0
07 | SUB TOTAL FOR STRUCTURAL STEEL WORK ETH BIRR |  |  |  | 0
08 | WALL AND FLOOR FINISHINGS
8.1 | PLASTERING & POINTING
Finishing work includes all surface pre cleaning, removal of mortar by chiseling, making good edges of columns and beams, preparation of grooves b/n surface where ever indicated, preparation and application of finish, polishing and cleaning after end of work.
8.1.1 | Cement Mortar Plastering to internal wall. plaster shall be applied in two coats of mortar with the following ratio: First coat: 1 Part cement to 2.5 parts aggregate by volume. Second Coat: 1 Part of cement to 3 parts of aggregate by volume. The work includes chiseling for vertical concrete wall, columns and vertical beams. | m2 | 468.32 |  | 0
8.1.2 | Gypsum Plaster (plaster of Paris) to internal wall: Plaster shall be applied in one coat of 3mm thick gypsum : The final fine coat gypsum plaster to be applied by trowel shall consist of one part of gypsum to three parts of lime putty, applied to a thickness of 3mm. The plaster shall be finished truly level and smooth. The plaster shall be allowed to cure. No finish shall be applied to gypsum plaster before the age of 28 days. | m2 | 468.32 |  | 0
8.1.3 | Cement Mortar Plaster to External wall: Plaster shall be applied in three coats of mortar with a ratio of 1:3. The final coat of cement plaster to be applied on two coat plaster shall consist of one part of cement to two parts of fine aggregate complying to BS 1199 by volume applied by trowel to a maximum thickness of 3mm. The surface shall be finished truly level and smooth. This coat shall be cured by watering for a minimum of seven days and allowed to cure for at least 28 days before further finish is applied on it. | m2 | 113.15 |  | 0
8.2 | Wall and floor finish
8.2.1 | Supply and fix 600X600X10mm Porcelain ceramic floor tiles of approved sizes and quality with cement mortar backing and joints grouted in colored cement. Pattern, color and quality shall be approved by the Engineer. | m2 | 119.645 |  | 0
8.2.2 | 100x10mm porcelain ceramic skirting stuck to wall with cement mortar (1:3)mix. | Lm | 94.75 |  | 0
8.2.3 | Supply and fix 300X300X8mm Non slippery ceramic floor tiles of approved sizes and quality with cement mortar backing and joints grouted in colored cement. Pattern, color and quality shall be approved by the Engineer. | m2 | 5.94 |  | 0
8.2.4 | Supply and fix 300x200x6mm Ceramic wall tiles with cement mortar backing. Price shall include grouting with matching color and other necessary works. | m2 | 22.44 |  | 0
8.2.6 | 280x30mm throated and weathered Granite door and window sill bedded in cement mortar (1:3) mix. It shall be chamfered at the edge, provide water drip at bottom face of sill and 2% slope towards outside. All according to the Engineer's approval. | Lm | 62.05 |  | 0
08 | SUB TOTAL FINISHING WORK ETH BIRR |  |  |  | 0
09 | PAINTING
9.1 | Apply three coats of approved quality plastic paint. Price shall include pre-cleaning and preparation of surfaces.
9.1.1 | To all internal wall and ceiling surface. | m2 | 468.32 |  | 0
9.1.2 | To external wall surface. | m2 | 113.15 |  | 0
09 | SUB TOTAL PAINTING WORK ETH BIRR |  |  |  | 0
10 | SANITARY INSTALLATION WORKS
All fixtures, equipment, pipes & materials which are specified below shall subject to the Engineer's approval, based on Samples, Catalogues and/or Brochures presented by the contractor. Unit Price shall include all the necessary installation accessories and all assistance civil works there to for the proper installation and operation of the sanitary wares, pipe works and any other related sanitary works.
10.1 | SANITARY APPLIANCES INSTALLATION
10.1.1 | Supply and fix High quality Gold Dragon or equivalent brand Hand wash Basin. The fixture shall conform to BS5506-3 or equivalent institution. The mixing faucets, waste drain holes, bottle trap, waste fitting, connecting pieces, fixing, female attakini(60cm long) and supporting elements and all other accessories shall comply with relevant clauses of BS standard or equivalent institution. size:520x420mmx850 mm high | pcs | 4 |  | 0
10.1.3 | Supply and fix Turkish Type Water closet made of enameled sheet steel. The fixture shall conform to British Standard Specification. The waste fittings, connecting pieces, fixing and supporting elements and Complete with all the necessary accessories. | pcs | 2 |  | 0
10.1.4 | Supply and fix stainless steel Sink , double bowel, complete with trap, drain connection, drainage and over flow, heavy duty mixing faucet, plug, chain, etc. and all other necessary faucet, plug, chain, etc. and all other necessary accessories. Size:- 1500 x 500 x150mm (bowl depth) | pcs | 1 |  | 0
10.2 | WATER SUPPLY SYSTEM |  |  |  | 0
10.2.1 | Supply and install 10,000 liters capacity Fiber Glass water tank for ground reservoir with complete with required gate valves,Ø50mm , inlet(Ø50mm) and outlet pipe(Ø32mm), over flow (Ø40mm) & drain (Ø40mm), vent pipe and all the necessary accessories thereto. The tank shall be placed on flat surface concrete floor. | pcs | 1 |  | 0
10.2.2 | Supply and install Polypropylene Random Co-polymer resins (PP Type 3 raw material) PPR PN-20 to internal cold water distribution system as shown on the drawing. Complete with all the necessary fittings and accessories. All diameters specified here are internal (Nominal) diameters.
| a) Dia. 25 mm | ml | 35 |  | 0
10.2.3 | Supply and fix 15mm dia chrome plated brass quarter turn angle valves with chrome plated copper connecting pipe, union nut and chrome plated brass wall flanges, and accessories complete in all respects. The Angle valve should be capable resisting of PN-10 before hand wash basins, water closets and other fixtures. | pcs | 4 |  | 0
10.2.4 | Supply and fix PPR service valves of approved standard, capable of resisting PN-10 on internal branch and pipe inlet to toilet, bath room, etc.; of the following size and as where shown on the drawing. | pcs | 6 |  | 0
10.3 | WASTE WATER DRAINAGE SYSTEM |  |  |  | 0
All domestic waste, vent and storm water pipe lines shall be comply to BS 459, BS 4660, BS 5481 as appropriate, using double ring seals and gaskets complying with BS 2394 uPVC, PN-6 pipes and shall be provided with a minimum slope as stated in the drawing. Pipes and necessary fittings shall be standard quality and be free from damage during storage, construction and etc. Unit price shall include all the necessary assistance civil works, such as excavation cartaway, fixing or hanging to walls, beams or slabs. etc., necessary fittings such as bends, Y, etc. Storm water uPVC, PN-6 pipes shall resist the external temperature and the quality shall meet the purpose. Flushing and testing of waste water system. Flushing has to be done to clean the pipe line from debris and silts. All waste water Pipe shall be tested by water pressure of 1.5 meters head for minimum of Four Hours.
10.3.1 | Providing, laying and jointing of internal uPVC PN-6 waste pipes with all uPVC pipe fittings including jointing with solvent cement joints and testing of joints etc. according to where shown on the drawings. Complete with all the necessary fittings. Provide cleaning detail for all waste water riser pipes as per the detail drawing.
10.3.1.1 | Dia. 50 mm, Outer diameter | ml | 14.9 |  | 0
10.3.1.2 | Dia. 110 mm, Outer diameter | ml | 12 |  | 0
10.3.1.3 | Dia. 160 mm, Outer diameter | ml | 15 |  | 0
10.3.2 | Providing, laying and jointing of uPVC PN-6 storm
water down pipes with all uPVC pipe fittings
including jointing with solvent cement joints and
testing of joints etc. according to where shown on
the drawings. Complete with all the necessary
fittings.
10.3.2.1 | Dia. 110 mm, Outer diameter | ml | 93.2 |  | 0
10.3.3 | Supply and construct Dia 300mm half concrete Open pipe for the Storm Water. Price shall include Excavation, 100mm thick red ash base and cement mortar mix (1:3) Side joint. The Work includes Connecting to External ditch. | ml | 40 |  | 0
10.3.3 | Supply Concrete Drain Cover 100x30x20cm C-25. Price shall include cement mortar mix (1:3) Side joint and all other related Works. | ml | 3 |  | 0
10.4 | Manhole
10.4.1 | Manhole in bricks jointed in cement mortar mix ( 1:3) and with concrete base internally of 700x700x700mm including concrete cover with lifting hole. | pcs | 2 |  | 0
10 | SUB TOTAL FOR SANITARY WORK ETH BIRR |  |  |  | 0
11 | ELECTRICAL INSTALLATION
11.3 | Switch Board
11.3.1 | Main Switch Board (MDB) in sheet steel enclosure, floor standing with lockable door including bus bars of 3x25Amp, 3 Phase rating, neutral and earth bars, connection terminals, complete and consisting of:-
7pcs,16A,MCB,1Phase
7pcs,10A,MCB,1Phase
| Including 25% reserve pitches | No | 1 |  | 0
11.4 | Feeder Power Cables
11.4.1 | Multi-core power cable copper conductor, color coded, in CABLE SHAF, connected and tested, all as specified and as shown on drawings
CABLES
11.4.1.1 | 3x4mm sq. | lm | 30 |  | 0
PVC PIPES
11.4.1.2 | PVC conduit of 16 mm diameter | lm | 30 |  | 0
11.5 | Extra Over Light Points for Switches
11.5.1 | Flush mounted Single switch points fed through PVC insulated conductors of 2x2.5mm2 inside PVC conduits of 16mm diameter, including junction boxes | No | 9 |  | 0
11.6 | Light Points
11.6.1 | Flush mounted light points fed through PVC insulated conductors of 3x2.5mm2 inside PVC conduits of 16mm diameter, including junction boxes with covers and insulating screw cap connectors. | No | 18 |  | 0
11.7 | Extra Over Light Points for Flush Mounted Switches
11.7.1 | Flush mounting single switch 774001+774041 | No | 9 |  | 0
11.8 | Flush Mounted Socket Outlet Points
11.8.1 | 16A/1P socket outlet points fed through PVC insulated conductors of 3x2.5mm2 inside PVC conduit of 16mm diameter including junction boxes with covers and insulating screw cap connectors. | No | 21 |  | 0
11.9 | Flush Mounted Socket Outlets with Earth Contact
11.9.1 | Flush mounting socket outlet of 16A 1Phase. | No | 21 |  | 0
11.1 | Lighting fitting
Supply, Connect and test including lamps and complete accessories, all as specified or described in lighting fittings schedule and as shown on the drawings.
11.10.1 | LED Ceiling lamp, 25W, dia 380mm for Rooms. | No | 14 |  | 0
11.10.2 | LED Ceiling lamp, 18W, dia 330mm waterproof for Toilets. | No | 4 |  | 0
11 | SUB TOTAL FOR ELECTRICAL WORK ETH BIRR |  |  |  | 0

## TO-1
Description
Excavation and Earthwork
Site Clearing
14.3
| 13.05 | 186.615
| 2.4 |  | Corridor to Pediatric Unit
| 1.95 | 4.68
|  | 191.295 | m2
Bulk Excavation, depth <= 80cm
14.3
13.05
| 0.8 | 149.3
2.4
| 1.95 |  | Corridor to Pediatric Unit
| 0.8 | 3.75
|  | 153.05 | m3
Pit Excavation
| 1.5 |  | F1
14 | 1.5
| 1 | 31.5
|  | 31.5 | m3
Trench Excavation to a depth of 1.5m
2 | 12.3
0.7
| 0.5 | 8.61
2 | 11.05
0.7
| 0.5 | 7.74
2 | 2.4
0.7
| 0.5 | 1.68
|  | 18.03 | m3
Backfill with granular material
| 202.58 |  | Bulk Excv +Pit Excv + Trench Excv
| 48.8496 |  | Volume of Concrete and Masonry works
153.7304
|  | 153.7304 | m3
Disposal works
| 240.839 |  | Clearing of fertile soil
|  | 240.84 | m3
Hardcore
1 | 5.5
| 3 | 16.5
1 | 1.8
| 3 | 5.4
1 | 3.6
| 3 | 10.8
2 | 5.6
| 1.55 | 17.36
2 | 5.6
| 5.1 | 57.12
1 | 2.275
| 1.25 | 2.85
|  | 110.03 | m2
Stone Masonry
2 | 12.3
1.5
| 0.5 | 18.45
2 | 11.05
1.5
| 0.5 | 16.58
2 | 2.4
1.5
| 0.5 | 3.6
|  | 38.63 | m3
Concrete Works
C-5 Lean concrete
Under Footing Pad
14 | 1.1 |  | F1
| 1.1 | 16.94
|  | 16.94 | m2
Under Grade Beam
2 | 12.3 |  | Axis-2 & 3
| 0.25 | 6.15
1 | 11.05 |  | Axis B
| 0.25 | 2.7625
1 | 3 |  | Axis B'
| 0.25 | 0.75
|  | 9.6625 | m2
Under Stone Masonry
2 | 12.3
| 0.5 | 12.3
2 | 11.05
| 0.5 | 11.05
2 | 2.4
| 0.5 | 2.4
|  | 25.75 | m2
C-25 Concrete
Footing Pad
14 | 1 |  | F1
1
| 0.45 | 6.3
|  | 6.3 | m3
Columns
Foundation column
14 | 0.2 |  | C1
0.3
| 1.55 | 1.302
|  | 1.302 | m3
Ground column
14 | 0.2 |  | C1
0.3
| 3 | 2.52
2 | 0.2 |  | False Columns
0.2
| 3 | 0.24
|  | 2.76 | m3
Ground Floor Slab
110.03
|  | 110.03 | m2
BEAMS
GROUND BEAM
GB1
2 | 0.3
0.2
| 12.3 | 1.48
GB2
2 | 0.3
0.2
| 14.7 | 1.77
GB3
3 | 0.3
0.2
| 11.05 | 1.99
GB4
1 | 0.3
0.2
| 3.7 | 0.23
|  | 5.47 | m3
Toptie BEAM
TB1
2 | 0.3
0.2
| 12.3 | 1.48
TB2
2 | 0.3
0.2
| 14.7 | 1.77
TB3
3 | 0.3
0.2
| 11.05 | 1.99
TB4
1 | 0.3
0.2
| 3.7 | 0.23
|  | 5.47 | m3
FORMWORK
Footing Pad
F1
14 | 4 |  | P=4*1= 4m
| 0.45 | 25.2
|  | 25.2 | m2
COLUMNS
Foundation column
14 | 1 |  | C1
| 1.25 | 17.5
|  | 17.5 | m2
Ground column
14 | 1 |  | C1
| 3 | 42
2 | 0.8 |  | False Column
| 3 | 4.8
|  | 46.8 | m2
BEAMS
GROUND BEAM
GB1
External
2 | 0.3
| 12.3 | 7.38
Internal
0.3
2
| 10.8 | 6.48
GB2
4 | 0.3 |  | internal
| 14.1 | 16.92 | `
GB3
2 | 0.3 |  | External
| 11.05 | 6.63
4 | 0.3 |  | internal
| 10.25 | 12.3 | `
GB4
2 | 0.3 |  | internal
| 3.3 | 1.98 | `
|  | 51.69 | m2
Toptie BEAM
TTB1
External
2 | 0.3
| 12.3 | 7.38
Internal
0.3
2
| 10.8 | 6.48
TTB2
4 | 0.3 |  | Internal
| 14.1 | 16.92
TTB3
2 | 0.3 |  | External
| 11.05 | 6.63
4 | 0.3 |  | internal
| 10.25 | 12.3 | `
TTB4
2 | 0.3 |  | internal
| 3.3 | 1.98 | `
|  | 51.69 | m2
Expansion Joints
111.2
6.05
|  | 117.25 | m
FINISHING WORKS
1, HCB WORK
200mm thick
External wall
Axis 1
1 | 7.7
| 3 | 23.1
Deduct Openings
-2 | 1 |  | Windows W1
| 2 | -4
Windows W3
-2 | 0.4
| 0.4 | -0.32
Axis 4
1 | 11.7
| 3 | 35.1
Deduct Openings
Windows W1
-4 | 1
| 2 | -8
Axis A
1 | 10.15
| 3 | 30.45
Axis C
1 | 6.75
| 3 | 20.25
Axis B'
1 | 3.1
| 3 | 9.3
Deduct Openings
Windows W2
-2 | 3
| 0.4 | -2.4
Door D1
-1 | 1.55
| 2.8 | -4.34
|  | 99.14 | m2
Internal Partition
150mm thick
Axis 2
1 | 13.7
| 3 | 41.1
Deduct Openings
-1 | 0.75 |  | Door D3
| 2.8 | -2.1
Door D4
-1 | 0.75
| 2.8 | -2.1
Door D2
-1 | 1.5
| 2.8 | -4.2
Window W4
-1 | 1.2
| 2 | -2.4
Opening
-1 | 0.95
| 3 | -2.85
Axis 3
1 | 13.7
| 3 | 41.1
Deduct Openings
Door D2
-2 | 1.5
| 2.8 | -8.4
Window W4
-1 | 1.2
| 2 | -2.4
Axis B
1 | 5.4
| 3 | 16.2
Axis C
2 | 9.1
| 3 | 54.6
Axis A', A''
2 | 3.3
| 3 | 19.8
Toilet Partition
1 | 1.8
| 3 | 5.4
|  | 153.75 | m2
Summary
External Wall
200mm thick HCB
99.14
|  | 99.14 | m2
Internal Wall
150mm thick HCB
|  | 153.75 | Block A
|  | 153.75 | m2
|  | - | [5 empty] | Plastering
|  |  | 2. Plastering |  |  |  | Ground column |  |  |  | Toptie BEAM
|  | 99.14 | External plastering
|  | 406.64 | Internal Plastering | 16 | 0.5 |  | C1 |  |  |  | External
[5 empty] | 3 | 24 |  | 2 | 0.3
|  | 24 | Plastering for Columns | [5 empty] | 12.3 | 7.38
|  | 37.68 | forInternal Sides of Beams | [7 empty] | Internal
|  | 14.01 | External plastering for beam | [5 empty] | 0.3
|  | 61.68 | m2 |  |  |  |  | 2
[9 empty] | 10.8 | 6.48
|  |  | 3. Painting | [7 empty] | TTB2
|  | 468.32 | to internal wall, Columns |  |  | 24 | m2 | 4 | 0.3 |  | Internal
|  | 113.15 | to External surface | [5 empty] | 14.1 | 16.92
TTB3
|  |  | 4, Floor Finish |  |  |  |  | 2 | 0.3 |  | External
|  |  | Ceramic Tile | [5 empty] | 11.05 | 6.63
|  |  | Toilet |  |  |  |  | 4 | 0.3 |  | internal
|  | 1.8 | [6 empty] | 10.25 | 12.3 | `
|  | 3.3 | [8 empty] | TTB4
[8 empty] | 2 | 0.3 |  | internal
|  | 5.94 | m2 | [5 empty] | 3.3 | 1.98 | `
5.94
Porcelain tile
|  | 63.72 | Wards
|  | 22.785 | Corridor
|  | 9.405 | Procedure Room
|  | 9.735 | Milk Preparation
|  | 14 | Verandah
|  | 119.645 | m2
Porcelain Skirting
|  | 42.2 | Wards
|  | 20.05 | Corridor
|  | 10.55 | Procedure Room
|  | 15.95 | Milk Preparation
|  | 6 | Verandah
|  | 94.75 | [7 empty] | 51.69
Ceramic wall
Toilet
2 | 3.3
| 2.2 | 14.52
2 | 1.8
| 2.2 | 7.92
[10 empty] | 14.01 | External
[10 empty] | 37.68 | Internal
|  | 22.44 | m2
Windowsill
6 | 1 | 6 | W1
2 | 3 | 6 | W2
2 | 0.4 | 0.8 | W3
2 | 1.2 | 2.4 | W4
Doorsill
1 | 1.55 | 1.55 | D1
3 | 1.5 | 4.5 | D2
3 | 0.75 | 13.6 | D3
1 | 0.75 | 13.6 | D4
2 | 0.65 | 13.6 | D5
|  | 62.05 | m
ROOF WORK
EGA 400
|  | 77.49 | m2
|  | 73.185 | m2
150.675
Corridor
|  | 5.64 | m2
|  | 5.64 | m2
|  | 156.315 | m2
STEEL WORK
Truss Work
T1
RHS= 60X60X3mm
Top Member, L= 12.5m
3 | 5.3694
| 12.5 | 201.3525 | kg
Bottom Member, L= 9.8m
3 | 5.3694
| 12 | 193.2984 | kg
394.6509
Diagonal & Vertical Members
RHS= 50X50X2.5
L= 18m
3 | 3.7287
| 18 | 201.3525 | kg
Purlin
RHS 30X30X2
Top and Bottom Members
12 | 1.7584
| 11.2 | 236.329 | kg
12 | 1.7584
| 11 | 232.1088 | kg
Vertical Members
RHS 25X25X2
12 | 1.4444
| 2.55 | 44.1986 | kg
12 | 1.4444
| 2.55 | 44.1986 | kg
Corridor
T2
RHS= 40X40X2.5mm
Top Member, L= 2.5m
2 | 2.9438
| 2.5 | 14.7188 | kg
Bottom Member, L= 2.35m
2 | 2.9438
| 2.35 | 13.8356 | kg
28.5544
Diagonal & Vertical Members
RHS= 40X40X2.5
L= 0.4m
2 | 2.9438
| 0.4 | 2.355 | kg
Purlin
RHS 30X30X2
Top and Bottom Members
4 | 1.7584
| 3.8 | 26.7277 | kg
Vertical Members
RHS 25X25X2
4 | 1.4444
| 1.93 | 11.1508 | kg
Summary
T1
|  | 394.6509 | RHS 60X60X3
|  | 201.3525 | RHS 50X50X2.5
T2
|  | 28.5544 | RHS 60X60X3
|  | 2.355 | RHS 50X50X2.5
Purlins
|  | 495.1654 | RHS 30X30X2
|  | 99.548 | RHS 25X25X2

## Re-bar
No | Member | Shape | Dia | length | No of bar | No of member | Ø6 | Ø8 | Ø10 | Ø12 | Ø14 | Ø16 | Ø20 | Ø24
Block-A
Footing Pad
F-1
|  |  | 12 | 1.5 | 7 | 14 | Ø12: 147
|  |  | 12 | 1.5 | 7 | 14 | Ø12: 147
Columns
Foundation Column
|  |  | 14 | 3.05 | 4 | 14 | Ø14: 170.8
|  |  | 8 | 0.9 | 14 | 14 | Ø8: 176.4
Ground Column
|  |  | 14 | 4.5 | 4 | 16 | Ø14: 288
|  |  | 8 | 0.9 | 28 | 16 | Ø8: 403.2
Ground Floor Slab
|  |  | 8 | 5.5 | 13 | 1 | Ø8: 71.5
|  |  | 8 | 3 | 23 | 1 | Ø8: 69
|  |  | 8 | 1.8 | 13 | 1 | Ø8: 23.4
|  |  | 8 | 3 | 9 | 1 | Ø8: 27
|  |  | 8 | 3.6 | 13 | 1 | Ø8: 46.8
|  |  | 8 | 3 | 16 | 1 | Ø8: 48
|  |  | 8 | 5.6 | 8 | 2 | Ø8: 89.6
|  |  | 8 | 1.55 | 24 | 2 | Ø8: 74.4
|  |  | 8 | 5.6 | 22 | 2 | Ø8: 246.4
|  |  | 8 | 5.1 | 24 | 2 | Ø8: 244.8
| Corridor |  | 8 | 2.275 | 6 | 1 | Ø8: 13.65
|  |  | 8 | 1.25 | 11 | 1 | Ø8: 13.75
Beams
Grade Beam
| GB-1 |  | 14 | 9.8 | 2 | 2 | Ø14: 39.2
|  |  | 14 | 3.7 | 2 | 2 | Ø14: 14.8
|  |  | 14 | 6.8 | 2 | 2 | Ø14: 27.2
|  |  | 14 | 6.7 | 2 | 2 | Ø14: 26.8
|  | ST | 8 | 1 | 83 | 2 | Ø8: 166
| GB-2 |  | 14 | 12 | 2 | 2 | Ø14: 48
|  |  | 14 | 3.7 | 2 | 2 | Ø14: 14.8
|  |  | 14 | 9.175 | 2 | 2 | Ø14: 36.7
|  |  | 14 | 6.7 | 2 | 2 | Ø14: 26.8
|  | ST | 8 | 1 | 99 | 2 | Ø8: 198
| GB-3 |  | 14 | 11.55 | 2 | 3 | Ø14: 69.3
|  |  | 14 | 11.55 | 2 | 3 | Ø14: 69.3
|  | ST | 8 | 1 | 74 | 3 | Ø8: 222
| GB-4 |  | 14 | 4.2 | 2 | 1 | Ø14: 8.4
|  |  | 14 | 4.2 | 2 | 1 | Ø14: 8.4
|  | ST | 8 | 1 | 74 | 1 | Ø8: 74
Toptie Beam
| TTB-1 |  | 14 | 9.8 | 2 | 2 | Ø14: 39.2
|  |  | 14 | 3.7 | 2 | 2 | Ø14: 14.8
|  |  | 14 | 6.8 | 2 | 2 | Ø14: 27.2
|  |  | 14 | 6.7 | 2 | 2 | Ø14: 26.8
|  | ST | 8 | 1 | 83 | 2 | Ø8: 166
| TTB-2 |  | 14 | 12 | 2 | 2 | Ø14: 48
|  |  | 14 | 3.7 | 2 | 2 | Ø14: 14.8
|  |  | 14 | 9.175 | 2 | 2 | Ø14: 36.7
|  |  | 14 | 6.7 | 2 | 2 | Ø14: 26.8
|  | ST | 8 | 1 | 99 | 2 | Ø8: 198
| TTB-3 |  | 14 | 11.55 | 2 | 3 | Ø14: 69.3
|  |  | 14 | 11.55 | 2 | 3 | Ø14: 69.3
|  | ST | 8 | 1 | 74 | 3 | Ø8: 222
| TTB-4 |  | 14 | 4.2 | 2 | 1 | Ø14: 8.4
|  |  | 14 | 4.2 | 2 | 1 | Ø14: 8.4
|  | ST | 8 | 1 | 74 | 1 | Ø8: 74
|  |  | total length (m) |  |  |  | 0 | 2867.9 | 0 | 294 | 1238.2 | 0 | 0 | 0
|  |  | weight per meter(Kg/m) |  |  |  | 0.222 | 0.395 | 0.617 | 0.888 | 1.208 | 1.578 | 2.466 | 3.551
|  |  | total weight (kg) |  |  |  | 0 | 1132.8205 | 0 | 261.072 | 1495.7456 | 0 | 0 | 0
0

## Rebar (hidden)
| 8 | 10 | 12 | 14 | 16 | 20 | 24
Bm 3 | 246.4385 |  |  | 124.1
BM 2 | 120.3577 |  |  | 72.1
| 278.6538 |  |  | 135.18
Bm A | 63.8077 |  |  | 28.2
BM B | 128.6538 |  |  | 67.8
BM C | 128.0769 |  |  | 68.4
BM D | 128.0769 |  |  | 83.6
MB H | 200.7692 |  |  | 94.9
BM F | 122.3077 |  |  | 55.9
| 39.2308 |  |  | 25.85
BM E | 115.3846 |  |  | 63.7
BM G | 167.3077 |  |  |  | 53.8 | 123.2
BM 1 | 159.2308 |  |  | 33.4 | 41.6
| 57.6923 |  |  | 31.7
| 123.4615 |  |  |  | 26.6 | 34.2
BM 4 | 271.1538 |  |  | 68.15 | 71.6
BM 2 | 308.0769 |  |  |  | 70.5 | 76.3
| 140.7692 |  |  | 34 | 43.1
BM 3 | 182.3077 |  |  |  | 61.4 | 59.65
BM B | 245.7692 |  |  |  | 53.2 | 63
BM C | 265.3846 |  |  |  | 12.8 | 161.6
BM D | 276.9231 |  |  |  | 63.8 | 87.9
BM E | 152.3077 |  |  |  | 41.15 | 58.4
BM G | 227.3077 |  |  |  | 56.7 | 75.5
BM F | 191.5385 |  |  |  | 42.6 | 65.6
BM H | 189.2308 |  |  |  |  | 119.7
BM 1 Arc | 121.1538 |  |  |  | 8.1 | 115.2
BM 4 arc | 211.1538 |  |  |  | 18.2 | 213.8
BM I' | 139.6154 |  |  |  | 31.8 | 39.2
at elev 3, 8, 12
BM 1 | 626.5385 |  |  |  | 161.1 | 185.4
| 491.5385 |  |  |  | 124.8 | 211.8
BM 2 | 443.0769 |  |  |  |  | 356.1
| 408.4615 |  |  |  | 101.7 | 135.9
BM 3 | 1045.3846 |  |  |  |  | 649.5
BM C | 778.8462 |  |  |  | 187.8 | 219.3
BM 4 | 1125 |  |  |  | 291.6 | 349.5
BM D | 810 |  |  |  | 190.2 | 306.6
BM G | 681.9231 |  |  |  | 174.9 | 227.1
BM H | 571.1538 |  |  |  | 117.3 | 139.5
BM E | 363.4615 |  |  | 105.6 | 106.5
BM E&F | 369.2308 |  |  |  | 150.6 | 248.4
| 242.3077 |  |  |  | 61.2 | 177.6
BM E | 138.4615 |  |  |  | 30.6 | 53.4
BM A | 461.5385 |  |  | 25.8 | 336 | 57.6
BM 1&2 Arc | 706.1538 |  |  |  | 139.2 | 812.4
BM 4 arc | 634.6154 |  |  |  | 234 | 279.6
BM I' | 272.3077 |  |  |  | 94.2 | 128.4
TYP
BM 3 | 2090.7692 |  |  |  |  | 1299
BM 2 | 886.1538 |  |  |  |  | 712.2
| 816.9231 |  |  |  | 203.4 | 271.8
BM 1 | 630 |  |  |  | 84.6 | 194.4
BM H | 1142.3077 |  |  |  | 306.6 | 411
BM D | 1107.6923 |  |  |  | 355.2 | 232.8
BM F&G | 2450.7692 |  |  |  | 168.3 | 858
BM F | 572.3077 |  |  |  | 192 | 285.6
| 184.6154 |  |  |  |  | 155.4
BM 1 Arc | 1412.3077 |  |  |  | 278.4 | 1624.8
BM 4 arc | 1278.4615 |  |  |  | 234 | 726.6
BM C&I' | 1089.2308 |  |  |  | 376.8 | 513.6
Total | 28833.6808 | 0 | 0 | 1118.38 | 5397.95 | 13116.55 | 0