## Cover Page
SPECIFICATIONS AND BILL OF QUANTITIES WITH ENGINEERING ESTIMATE
PROJECT:
SUHUL SHIRE HOSPITAL WASTE DISPOSAL and WATER SUPPLY
LOCATION:
SHIRE - ETHIOPIA
OWNER:
DOCTORS WITH AFRICA- CUAMM
Prepared by:- Solomon Tesfay
2024-08-24

## Summary
SUHUL SHIRE Hoapital Solid Waste and Water Supply
SUMMARY OF PRICES
1. SOLID WASTE DISPOSAL | Birr | 0
2. WASTE WATER DRAINAGE SYSTEM | Birr | 0
3. WATER SUPPLY | Birr | 0
4. EXTERNAL TOILET | Birr | 0
SERVICE SUM | Birr | 0
15% VAT | Birr | 0
GRAND TOTAL | Birr | 0
2660
|  |  | 60 | 28500
60

## BOQ
BILL OF QUANTITY - SUHUL SHIRE Solid Waste & Water Supply
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | QUANTITY
01 | SOLID WASTE DISPOSAL
1.1 | WASTE DISPOSAL PIT
1.1.1 | Clearing Area around the perimeter of the Waste Diposal pit (12mx10m). The top soil shall be removed leaving area clear off any vegetable soil. The removal of top soil shall be measured by the area along the primeter of the waste pit with a width of 2 meters. Removal of top soil shall be understood as including the disposal of surplus material or stock piling and wheel spreading of top soil at later stages as directed by the Engineer. | m² | 104 |  | 0
1.2 | FENCE
1.2.1 | Supply and fix 1.8m high Fence for 12m x 10m x 5m Waste Disposal Pit with 2.5mm thick galvanized wire mesh having 50x50mm spacing and fixed to 40*40*3mm RHS post at 2m spacing buried in 50cm concrete foundation. Price shall include anchor works, diagonal bracings on both sides of every corner, excavation, cartaway, tying wire and two coats of synthetic paint to angle iron posts and bracings. | ml | 44 |  | 0
1.2.2 | Main gate made of Dia.2.5mm galvanized wire mesh fixed on 40x40x3mm RHS frames according to the detail drawing. Price shall include Dia. 40mm, 3mm thick CHS post embeded in C-15 concrete blocks size 500x500x500mm, one coat of antirust, two coats of synthetic paint chain locks and all the necessary accessories to complete the work. Gate size 1200x1800mm | pcs | 2 |  | 0
01 | SUB TOTAL FOR SOLID WASTE DISPOSAL ETH BIRR |  |  |  | 0
02 | WASTE WATER DRAINAGE SYSTEM
All domestic waste, vent and storm water pipe lines shall be comply to BS 459, BS 4660, BS 5481 as appropriate, using double ring seals and gaskets complying with BS 2394 uPVC, PN-6 pipes and shall be provided with a minimum slope as stated in the drawing. Pipes and necessary fittings shall be standard quality and be free from damage during storage, construction and etc. Unit price shall include all the necessary assistance civil works, such as excavation cartaway, fixing or hanging to walls, beams or slabs. etc., necessary fittings such as bends, Y, etc. Storm water uPVC, PN-6 pipes shall resist the external temperature and the quality shall meet the purpose. Flushing and testing of waste water system. Flushing has to be done to clean the pipe line from debris and silts. All waste water Pipe shall be tested by water pressure of 1.5 meters head for minimum of Four Hours.
2.1 | Clean Manholes
Remove blockages of the existing Sewarage Line of the Hospital by Cleaning all the Manholes of the Hospital. Price shall include all the necessary assistance civil works, such as excavation and cartaway.
2.1.1 | Circular Manholes D = 70cm with 3m Depth
2.1.1.1 | In-between Blocks | No | 8 |  | 0
2.1.1.2 | Around the Main Hospital | No | 28 |  | 0
2.1.1.3 | Around the Management Office | No | 10 |  | 0
2.1.1.4 | From Emergengy to the Main Gate | No | 4 |  | 0
2.1.1.5 | From the Main Gate to the Septic Tank | No | 4 |  | 0
2.1.2 | Rectangular Manholes 70x70cm with 1m Depth
2.1.2.1 | In-between Blocks (6 Manholes for each of the 8 blocks) | No | 48 |  | 0
2.1.2.2 | Around the Main Hospital | No | 8 |  | 0
2.2 | Substitute Existing uPVC Pipes with uPVC PN-6 waste pipes D = 200mm
Providing, laying and jointing of internal uPVC PN-6 waste pipes with all uPVC pipe fittings including jointing with solvent cement joints and testing of joints etc. Price shall include all the necessary fittings.
2.2.1 | In-between Blocks (6 Manholes for each of the 8 blocks) | ml | 240 |  | 0
2.3 | Clean Existing Septic Tank
Clean and Empty Existing overflowing Septic Tank. Price shall include all the necessary assistance civil works, such as excavation and cartaway and all other additional expenses.
2.3.1 | Concrete Septic Tank 20mx15m | LS | 1 |  | 0
02 | SUB TOTAL FOR WASTE WATER DRAINAGE SYSTEM ETH BIRR |  |  |  | 0
03 | WATER SUPPLY & DISTRIBUTION PLANT
3.1 | Repair Existing 10,000 liter Fiber Glass Tankers (2pcs) and connect it to existing water distribution of the Hospital. Price shall include all related piping work (inlet, outlet, drain, over flow ), valves and related civil works. | pcs | 2 |  | 0
03 | SUB TOTAL FOR WATER SUPPLY ETH BIRR |  |  |  | 0
04 | TOILET NEXT TO EMERGENCY
4.1 | PLASTERING & POINTING
Finishing work includes all surface pre cleaning, removal of mortar by chiseling, making good edges of columns and beams, preparation of grooves b/n surface where ever indicated, preparation and application of finish, polishing and cleaning after end of work.
4.1.1 | Cement Mortar Plaster to External wall: Plaster shall be applied in three coats of mortar with a ratio of 1:3. The final coat of cement plaster to be applied on two coat plaster shall consist of one part of cement to two parts of fine aggregate complying to BS 1199 by volume applied by trowel to a maximum thickness of 3mm. The surface shall be finished truly level and smooth. This coat shall be cured by watering for a minimum of seven days and allowed to cure for at least 28 days before further finish is applied on it. | m2 | 36.6 |  | 0
4.2 | WALL & FLOOR FINISH
4.2.1 | Supply and fix 600X600X10mm Porcelain ceramic floor tiles of approved sizes and quality with cement mortar backing and joints grouted in colored cement. Pattern, color and quality shall be approved by the Engineer. | m2 | 12 |  | 0
4.2.2 | Supply and fix 300x300x6mm Ceramic wall tiles with cement mortar backing for Handwash Area . Price shall include grouting with matching color and other necessary works. | m2 | 5.04 |  | 0
4.3 | PAINTING
4.3.1 | Supply and Apply three coats of weather resistant emulsion paint to External plastered wall surfaces. Cost includes clean both surfaces and fix all cracks with Masonry Filler. Color to be approved by the Architect/Engineer. | m2 | 76.75 |  | 0
04 | SUB TOTAL EXTERNAL TOILET ETH BIRR |  |  |  | 0

## Rebar (hidden)
| 8 | 10 | 12 | 14 | 16 | 20 | 24
Bm 3 | 246.4385 |  |  | 124.1
BM 2 | 120.3577 |  |  | 72.1
| 278.6538 |  |  | 135.18
Bm A | 63.8077 |  |  | 28.2
BM B | 128.6538 |  |  | 67.8
BM C | 128.0769 |  |  | 68.4
BM D | 128.0769 |  |  | 83.6
MB H | 200.7692 |  |  | 94.9
BM F | 122.3077 |  |  | 55.9
| 39.2308 |  |  | 25.85
BM E | 115.3846 |  |  | 63.7
BM G | 167.3077 |  |  |  | 53.8 | 123.2
BM 1 | 159.2308 |  |  | 33.4 | 41.6
| 57.6923 |  |  | 31.7
| 123.4615 |  |  |  | 26.6 | 34.2
BM 4 | 271.1538 |  |  | 68.15 | 71.6
BM 2 | 308.0769 |  |  |  | 70.5 | 76.3
| 140.7692 |  |  | 34 | 43.1
BM 3 | 182.3077 |  |  |  | 61.4 | 59.65
BM B | 245.7692 |  |  |  | 53.2 | 63
BM C | 265.3846 |  |  |  | 12.8 | 161.6
BM D | 276.9231 |  |  |  | 63.8 | 87.9
BM E | 152.3077 |  |  |  | 41.15 | 58.4
BM G | 227.3077 |  |  |  | 56.7 | 75.5
BM F | 191.5385 |  |  |  | 42.6 | 65.6
BM H | 189.2308 |  |  |  |  | 119.7
BM 1 Arc | 121.1538 |  |  |  | 8.1 | 115.2
BM 4 arc | 211.1538 |  |  |  | 18.2 | 213.8
BM I' | 139.6154 |  |  |  | 31.8 | 39.2
at elev 3, 8, 12
BM 1 | 626.5385 |  |  |  | 161.1 | 185.4
| 491.5385 |  |  |  | 124.8 | 211.8
BM 2 | 443.0769 |  |  |  |  | 356.1
| 408.4615 |  |  |  | 101.7 | 135.9
BM 3 | 1045.3846 |  |  |  |  | 649.5
BM C | 778.8462 |  |  |  | 187.8 | 219.3
BM 4 | 1125 |  |  |  | 291.6 | 349.5
BM D | 810 |  |  |  | 190.2 | 306.6
BM G | 681.9231 |  |  |  | 174.9 | 227.1
BM H | 571.1538 |  |  |  | 117.3 | 139.5
BM E | 363.4615 |  |  | 105.6 | 106.5
BM E&F | 369.2308 |  |  |  | 150.6 | 248.4
| 242.3077 |  |  |  | 61.2 | 177.6
BM E | 138.4615 |  |  |  | 30.6 | 53.4
BM A | 461.5385 |  |  | 25.8 | 336 | 57.6
BM 1&2 Arc | 706.1538 |  |  |  | 139.2 | 812.4
BM 4 arc | 634.6154 |  |  |  | 234 | 279.6
BM I' | 272.3077 |  |  |  | 94.2 | 128.4
TYP
BM 3 | 2090.7692 |  |  |  |  | 1299
BM 2 | 886.1538 |  |  |  |  | 712.2
| 816.9231 |  |  |  | 203.4 | 271.8
BM 1 | 630 |  |  |  | 84.6 | 194.4
BM H | 1142.3077 |  |  |  | 306.6 | 411
BM D | 1107.6923 |  |  |  | 355.2 | 232.8
BM F&G | 2450.7692 |  |  |  | 168.3 | 858
BM F | 572.3077 |  |  |  | 192 | 285.6
| 184.6154 |  |  |  |  | 155.4
BM 1 Arc | 1412.3077 |  |  |  | 278.4 | 1624.8
BM 4 arc | 1278.4615 |  |  |  | 234 | 726.6
BM C&I' | 1089.2308 |  |  |  | 376.8 | 513.6
Total | 28833.6808 | 0 | 0 | 1118.38 | 5397.95 | 13116.55 | 0