## Cover Page
SPECIFICATIONS AND BILL OF QUANTITIES WITH ENGINEERING ESTIMATE
PROJECT:
WATER SUPPLY AND DISTRIBUTION WORKS ENDABAGUNA HOSPITAL and 2 HEALTH CENTERS
LOCATION:
SHIRE, TIGRAY, ETHIOPIA
OWNER:
DOCTORS WITH AFRICA- CUAMM
Prepared by:- Solomon Tesfay
2025-07-15

## GRAND Summary
GRAND SUMMARY
LOT 2&3
ALGANESH HEALTH CENTER | Birr | 0
FIVE ANGELS HEALTH CENTER | Birr | 0
ENDABAGUNA HOSPITAL | Birr | 0
TOTAL | Birr | 0
15% VAT | Birr | 0
GRAND TOTAL | Birr | 0
2660
|  |  | 60 | 28500
60

## ALGANESH HC Summary
ALGANESH HEALTH CENTER
SUMMARY OF PRICES
01. WATER WELL | Birr | 0
02. WASTE WATER DRAINAGE SYSTEM | Birr | 0
03. WATER SUPPLY and DISTRIBUTION | Birr | 0
| Birr | 0
15% VAT | Birr | 0
GRAND TOTAL | Birr | 0
2660
|  |  | 60 | 28500
60

## ALGANESH HC
BILL OF QUANTITY - Alganesh Health Center
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | QUANTITY
01 | WATER WELL
Based on actual field observations and previously collected geophysical investigation and interpretation one borehole site is identified. The site should be drilled to a depth of 100m but the actual depth of the drilling should be determined during supervision based on the actual findings. The drilling diameter should be 141/2" bit for the top or soft formation (10m) and the remaining 90m has to be drilled by 103/4" drilling bit. The recommended temporary and permanent surface casing is 12" Steel while the production casing should be in PVC and with 6" internal diameter. The well should be packed with appropriately sieved, well rounded and sorted river gravel (6-9 mm). A 3/4" galvanized steel observation pipe should be installed to a depth of maximum anticipated drawdown in the annular space of the borehole that helps to monitor the water level. The well should be developed until it becomes clear and free of any fine particles.
The Contractor shall supply capable and experienced personnel, including hydrogeologists, chief drillers, and deploy a modern and good capacity hydraulic MUD/DTH and/or direct circulation rotary drill rig.
Price should include all the necessary permits from the Authorities (Woreda and/or Regional Offices), Mobilization/Demobilization (transportation of materials, equipment, accessories, crew members for constructing and developing the well to and from the site, pump test equipment), preparation of lithological log, well cleaning and disinfection with hydrochloride, Water Sampling and Quality Analysis, Supply and Installation of tagging plate and final Technical Report in English.
1.1 | Drilling
1.1.1 | Drilling in All formation, DTH/MUD 141/2 inch external bit diameter | ml | 10 |  | 0
1.1.2 | Drilling in All formation, DTH 103/4 inch external bit diameter | ml | 90 |  | 0
1.2 | Supply and Installation of Casings
1.2.1 | Supply and Install 12" Steel Temporary surface casing | ml | 10 |  | 0
1.2.2 | Supply and Install 12" Steel Permanent surface casing | ml | 10 |  | 0
1.2.3 | Supply and Install 6" ID PVC blind casing | ml | 60 |  | 0
1.2.4 | Supply and Install 6" ID PVC screen casing | ml | 40 |  | 0
1.3 | Gravel Packing and Well Construction
1.3.1 | Supply and pack selected river gravel | m3 | 8 |  | 0
1.3.2 | Grout with mass concrete to a depth not exceeding 10m and construct well head (0.8x0.5x0.4m) C-25 concrete | LS | 1 |  | 0
1.3.3 | Supply and Install 3/4" observation pipe (GSP) | ml | 78 |  | 0
1.3.4 | Supply and weld iron cover on top of borehole | LS | 1 |  | 0
1.4 | Pumping Test
1.4.1 | Step-draw dawn test (Four steps of 2 hours duration) | Hrs | 8 |  | 0
1.4.3 | Constant Discharge test | Hrs | 24 |  | 0
1.4.4 | Recovery Test | Hrs | 12 |  | 0
01 | SUB TOTAL FOR WATER WELL ETH BIRR |  |  |  | 0
02 | WASTE WATER DRAINAGE SYSTEM
All waste water pipe lines shall be uPVC pipes and shall be provided with a slope of 2% or as indicated on the drawings towards the outlet. All uPVC pipes and necessary fittings shall be standard quality and be free from damage during storage, construction and etc. Unit price shall include all the necessary assistance civil works, such as excavation cartaway, fixing or hanging to walls, beams or slabs. etc., necessary fittings such as bends, Y, T, etc.
2.1 | Remove blockages of the existing Sewerage Line of the Hospital by Cleaning all the Manholes, Substituting the Damaged uPVC Pipes with uPVC PN-6 waste pipes D =160mm and Cleaning the Existing Septic Tanks. Price shall include all the necessary assistance civil works, such as excavation, cartaway and all the necessary fittings. | LS | 1 |  | 0
02 | SUB TOTAL FOR WASTE WATER DRAINAGE SYSTEM ETH BIRR |  |  |  | 0
03 | WATER SUPPLY & DISTRIBUTION
3.1 | Water Distribution
3.1.1 | Maintainance of the water distribution of the Hospital. Price shall include all related piping work (inlet, outlet, drain, over flow ), valves and related civil works. | LS | 1 |  | 0
3.2 | Submersible Pump
3.2.1 | Supply, install, test and commission GRUNDFOS or Equivalent solar pump to the existing water well. The pump should come with a controller and selector to enable it to work with AC+Solar. Price shall include all the necessary fittings and solar accessories. The pump should have the following specifications:
Rated Flow = 5 m3/h
Rated Head = 100 m /shall be revised after drilling the well/
Rated Power = 2KW - 3 KW
Efficiency > 80%
NPSH > 1.5m
|  | Set | 1 |  | 0
3.2.2 | Supply and install 1.5 inch HDPE, PN16 pipe for bore well with approximately 60 meters depth. Complete with all the necessary fittings and accessories. | LS | 1 |  | 0
3.3 | Water Distribution
3.3.1 | Connect the pump with the existing elevated 10,000 liter Fiber Glass Tanker so as to enhance the water distribution of the Health center. The following accessories shall be incorporated with each water tanks: Float valve, Drain pipe, PN10 Bronze Gate Valve on Drain valve, Overflow pipe, Automatic level control switch, PN10 Bronze Gate Valve after tank, PN10 Bronze Gate Valve before. Price shall include all related piping work (inlet, outlet, drain, over flow), valves and related civil works. | LS | 1 |  | 0
3.3.2 | Connect Elevated Water Tanker with Existing 10,000 liter Fiber Glass Tanker so as to enhance the water distribution of the Hospital. Moreover the following accessories shall be incorporated to the tankers: Float valve, Drain pipe, PN10 Bronze Gate Valve on Drain valve, Overflow pipe, Automatic level control switch, PN10 Bronze Gate Valve after tank, PN10 Bronze Gate Valve before. Price shall include all related piping work (inlet, outlet, drain, over flow), valves and related civil works. | No | 1 |  | 0
03 | SUB TOTAL FOR WATER SUPPLY ETH BIRR |  |  |  | 0

## FIVE ANGELS HC Summary
FIVE ANGELS HEALTH CENTER
SUMMARY OF PRICES
01. WATER WELL | Birr | 0
02. WASTE WATER DRAINAGE SYSTEM | Birr | 0
03. WATER SUPPLY and DISTRIBUTION | Birr | 0
| Birr | 0
15% VAT | Birr | 0
GRAND TOTAL | Birr | 0
2660
|  |  | 60 | 28500
60

## FIVE ANGELS HC
BILL OF QUANTITY - FIVE ANGELS Health Center
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | QUANTITY
1 | WATER WELL
Based on actual field observations and previously collected geophysical investigation and interpretation one borehole site is identified. The site should be drilled to a depth of 100m but the actual depth of the drilling should be determined during supervision based on the actual findings. The drilling diameter should be 141/2" bit for the top or soft formation (10m) and the remaining 90m has to be drilled by 103/4" drilling bit. The recommended temporary and permanent surface casing is 12" Steel while the production casing should be in PVC and with 6" internal diameter. The well should be packed with appropriately sieved, well rounded and sorted river gravel (6-9 mm). A 3/4" galvanized steel observation pipe should be installed to a depth of maximum anticipated drawdown in the annular space of the borehole that helps to monitor the water level. The well should be developed until it becomes clear and free of any fine particles.
The Contractor shall supply capable and experienced personnel, including hydrogeologists, chief drillers, and deploy a modern and good capacity hydraulic MUD/DTH and/or direct circulation rotary drill rig.
Price should include all the necessary permits from the Authorities (Woreda and/or Regional Offices), Mobilization/Demobilization (transportation of materials, equipment, accessories, crew members for constructing and developing the well to and from the site, pump test equipment), preparation of lithological log, well cleaning and disinfection with hydrochloride, Water Sampling and Quality Analysis, Supply and Installation of tagging plate and final Technical Report in English.
1.1 | Drilling
1.1.1 | Drilling in All formation, DTH/MUD 141/2 inch external bit diameter | ml | 10 |  | 0
1.1.2 | Drilling in All formation, DTH 103/4 inch external bit diameter | ml | 90 |  | 0
1.2 | Supply and Installation of Casings
1.2.1 | Supply and Install 12" Steel Temporary surface casing | ml | 10 |  | 0
1.2.2 | Supply and Install 12" Steel Permanent surface casing | ml | 10 |  | 0
1.2.3 | Supply and Install 6" ID PVC blind casing | ml | 60 |  | 0
1.2.4 | Supply and Install 6" ID PVC screen casing | ml | 40 |  | 0
1.3 | Gravel Packing and Well Construction
1.3.1 | Supply and pack selected river gravel | m3 | 8 |  | 0
1.3.2 | Grout with mass concrete to a depth not exceeding 10m and construct well head (0.8x0.5x0.4m) C-25 concrete | LS | 1 |  | 0
1.3.3 | Supply and Install 3/4" observation pipe (GSP) | ml | 78 |  | 0
1.3.4 | Supply and weld iron cover on top of borehole | LS | 1 |  | 0
1.4 | Pumping Test
1.4.1 | Step-draw dawn test (Four steps of 2 hours duration) | Hrs | 8 |  | 0
1.4.3 | Constant Discharge test | Hrs | 24 |  | 0
1.4.4 | Recovery Test | Hrs | 12 |  | 0
01 | SUB TOTAL FOR WATER WELL ETH BIRR |  |  |  | 0
02 | WASTE WATER DRAINAGE SYSTEM
All waste water pipe lines shall be uPVC pipes and shall be provided with a slope of 2% or as indicated on the drawings towards the outlet. All uPVC pipes and necessary fittings shall be standard quality and be free from damage during storage, construction and etc. Unit price shall include all the necessary assistance civil works, such as excavation cartaway, fixing or hanging to walls, beams or slabs. etc., necessary fittings such as bends, Y, T, etc.
2.1 | Remove blockages of the existing Sewerage Line of the Hospital by Cleaning all the Manholes, Substituting the Damaged uPVC Pipes and Cleaning the Existing Septic Tanks. Price shall include all the necessary assistance civil works, such as excavation, cartaway and all the necessary fittings. | LS | 1 |  | 0
02 | SUB TOTAL FOR WASTE WATER DRAINAGE SYSTEM ETH BIRR |  |  |  | 0
03 | WATER SUPPLY & DISTRIBUTION
3.1 | Submersible Pump
3.1.1 | Supply, install, test and commission GRUNDFOS or Equivalent solar pump to the existing water well. The pump should come with a controller and selector to enable it to work with AC+Solar. Price shall include all the necessary fittings and solar accessories. The pump should have the following specifications:
Rated Flow = 5 m3/h
Rated Head = 100 m /shall be revised after drilling the well/
Rated Power = 2KW - 3 KW
Efficiency > 80%
NPSH > 1.5m
|  | Set | 1 |  | 0
3.1.2 | Supply and install 1.5 inch HDPE, PN16 pipe for bore well with approximately 60 meters depth. Complete with all the necessary fittings and accessories. | LS | 1 |  | 0
3.2 | Water Distribution
3.2.1 | Connect the pump with the existing elevated 10,000 liter Fiber Glass Tanker so as to enhance the water distribution of the Health center. The following accessories shall be incorporated with each water tanks: Float valve, Drain pipe, PN10 Bronze Gate Valve on Drain valve, Overflow pipe, Automatic level control switch, PN10 Bronze Gate Valve after tank, PN10 Bronze Gate Valve before. Price shall include all related piping work (inlet, outlet, drain, over flow), valves and related civil works. | LS | 1 |  | 0
03 | SUB TOTAL FOR WATER SUPPLY ETH BIRR |  |  |  | 0

## ENDABAGUNA Summary
ENDABAGUNA HOSPITAL
SUMMARY OF PRICES
Phase 1 - LOT 3
1. WATER SUPPLY | Birr | 0
2. DRAINAGE WATER SYSTEM REPAIR | Birr | 0
3. FENCE FOR THE BOREHOLE | Birr | 0
| Birr | 0
15% VAT | Birr | 0
GRAND TOTAL | Birr | 0
2660
|  |  | 60 | 28500
60

## BoQ
BILL OF QUANTITY - ENDABAGUNA HOSPITAL
Phase 1 - Lot 3
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | QUANTITY
01 | WATER SUPPLY
1.1 | Submersible Pump
1.1.1 | Supply, install, test and commission GRUNDFOS or Equivalent solar pump to the existing water well. The pump should come with a controller and selector to enable it to work with AC+Solar. Price shall include all the necessary fittings and solar accessories. The pump should have the following specifications:
Rated Flow = 5 m3/h
Rated Head = 73 m
Rated Power = 1.85 kW
Efficiency > 80%
NPSH > 1.5m
|  | Set | 1 |  | 0
1.1.2 | Supply and install 1.5 inch HDPE, PN16 pipe for hand dug shallow well with 18 - 20 meters depth. Complete with all the necessary fittings and accessories. | LS | 1 |  | 0
01 | SUB TOTAL FOR WATER SUPPLY ETH BIRR |  |  |  | 0
02 | Drainage Water System Maintainance
2.1 | Remove blockages of the existing drainage Line by Cleaning all the Manholes, pipe lines of the Hospital. Price shall include all the necessary assistance civil works, replacement of the broken pipes, replacement of the missing items and all necessary items needed for the drainage water flow. | LS | 1 |  | 0
02 | SUB TOTAL FOR DRAINAGE WATER SYSTEM ETH BIRR |  |  |  | 0
03 | FENCE FOR THE BOREHOLE
3.1 | Supply and fix 2m high Fence with a dimension of 6m x 8m for the water well with 2.5mm thick galvanized wire mesh having 50x50mm spacing and fixed to 40*40*2mm RHS post at 2m spacing buried in 25cm concrete foundation and surrounded by a razor wire on the top. The bottom part of the Fence should be supported with a 20cm thick concrete. Price shall include anchor works, diagonal bracings on both sides of every corner, excavation, cartaway, tying wire, concrte works, razor wires and two coats of synthetic paint to RHS posts and bracings. | ml | 28 |  | 0
3.2 | Metalic gate made of Dia.2.5mm galvanized wire mesh fixed on 40x40x2mm RHS frames according to the detail drawing. Price shall include hinges, latches, dor locks, one coat of antirust, two coats of synthetic paint chain locks and all the necessary accessories to complete the work. Gate size 1000x2000mm | pcs | 1 |  | 0
03 | SUB TOTAL FOR FENCE FOR THE BOREHOLE ETH BIRR |  |  |  | 0

## Rebar (hidden)
| 8 | 10 | 12 | 14 | 16 | 20 | 24
Bm 3 | 246.4385 |  |  | 124.1
BM 2 | 120.3577 |  |  | 72.1
| 278.6538 |  |  | 135.18
Bm A | 63.8077 |  |  | 28.2
BM B | 128.6538 |  |  | 67.8
BM C | 128.0769 |  |  | 68.4
BM D | 128.0769 |  |  | 83.6
MB H | 200.7692 |  |  | 94.9
BM F | 122.3077 |  |  | 55.9
| 39.2308 |  |  | 25.85
BM E | 115.3846 |  |  | 63.7
BM G | 167.3077 |  |  |  | 53.8 | 123.2
BM 1 | 159.2308 |  |  | 33.4 | 41.6
| 57.6923 |  |  | 31.7
| 123.4615 |  |  |  | 26.6 | 34.2
BM 4 | 271.1538 |  |  | 68.15 | 71.6
BM 2 | 308.0769 |  |  |  | 70.5 | 76.3
| 140.7692 |  |  | 34 | 43.1
BM 3 | 182.3077 |  |  |  | 61.4 | 59.65
BM B | 245.7692 |  |  |  | 53.2 | 63
BM C | 265.3846 |  |  |  | 12.8 | 161.6
BM D | 276.9231 |  |  |  | 63.8 | 87.9
BM E | 152.3077 |  |  |  | 41.15 | 58.4
BM G | 227.3077 |  |  |  | 56.7 | 75.5
BM F | 191.5385 |  |  |  | 42.6 | 65.6
BM H | 189.2308 |  |  |  |  | 119.7
BM 1 Arc | 121.1538 |  |  |  | 8.1 | 115.2
BM 4 arc | 211.1538 |  |  |  | 18.2 | 213.8
BM I' | 139.6154 |  |  |  | 31.8 | 39.2
at elev 3, 8, 12
BM 1 | 626.5385 |  |  |  | 161.1 | 185.4
| 491.5385 |  |  |  | 124.8 | 211.8
BM 2 | 443.0769 |  |  |  |  | 356.1
| 408.4615 |  |  |  | 101.7 | 135.9
BM 3 | 1045.3846 |  |  |  |  | 649.5
BM C | 778.8462 |  |  |  | 187.8 | 219.3
BM 4 | 1125 |  |  |  | 291.6 | 349.5
BM D | 810 |  |  |  | 190.2 | 306.6
BM G | 681.9231 |  |  |  | 174.9 | 227.1
BM H | 571.1538 |  |  |  | 117.3 | 139.5
BM E | 363.4615 |  |  | 105.6 | 106.5
BM E&F | 369.2308 |  |  |  | 150.6 | 248.4
| 242.3077 |  |  |  | 61.2 | 177.6
BM E | 138.4615 |  |  |  | 30.6 | 53.4
BM A | 461.5385 |  |  | 25.8 | 336 | 57.6
BM 1&2 Arc | 706.1538 |  |  |  | 139.2 | 812.4
BM 4 arc | 634.6154 |  |  |  | 234 | 279.6
BM I' | 272.3077 |  |  |  | 94.2 | 128.4
TYP
BM 3 | 2090.7692 |  |  |  |  | 1299
BM 2 | 886.1538 |  |  |  |  | 712.2
| 816.9231 |  |  |  | 203.4 | 271.8
BM 1 | 630 |  |  |  | 84.6 | 194.4
BM H | 1142.3077 |  |  |  | 306.6 | 411
BM D | 1107.6923 |  |  |  | 355.2 | 232.8
BM F&G | 2450.7692 |  |  |  | 168.3 | 858
BM F | 572.3077 |  |  |  | 192 | 285.6
| 184.6154 |  |  |  |  | 155.4
BM 1 Arc | 1412.3077 |  |  |  | 278.4 | 1624.8
BM 4 arc | 1278.4615 |  |  |  | 234 | 726.6
BM C&I' | 1089.2308 |  |  |  | 376.8 | 513.6
Total | 28833.6808 | 0 | 0 | 1118.38 | 5397.95 | 13116.55 | 0